## Table 1-1
Table 1-1: PSPS Event Summary
Total Customers |  |  | De-energized |  |  |  | Number of Circuits |  |  | Damage/Hazard Count
PSPS Notified | De-energized | Cancelled | MBL Customers | Number of Counties | Number of Tribes | Critical Facilities and Infrastructure | Transmission De-energized | Distribution Circuits in Scope | Distribution Circuits De-energized
1,443[1] | 1443 | 0 | 13 | 2 | 1 | 75 | 0 | 2 | 2 | 3
[1] Liberty’s post event report includes a lower customer count compared to its in-event reporting. This is because Liberty’s in-event reporting (i.e., initial count of customers) includes disconnected accounts and duplicate accounts. As seen during this event, Liberty’s initial customer count numbers may be higher than actuals as it reports the maximum potential impacted customers and attempts to communicate with as many customers as possible. Liberty’s customer notification system automatically suppresses duplicates and would not include notifications to disconnected accounts.

## Table 2-1
Table 2-1: Factors Considered in Decision to De-Energize
Circuit De-energized | Sustained Wind Speed (mph) | Gust Wind Speed (mph) | Relative Humidity (%) | FFWI | Live Woody Fuel Moisture | 1000hr Fuel Moisture (%)
Muller 1296 | 30-40 | 60 | 20 | 60 | 71% | 9%
Topaz 1202 | 30-40 | 60 | 20 | 60 | 71% | 9%

## Table 3-1
Table 3-1: PSPS Event Summary
Circuits De-Energized
County | Circuit Name | De-energization Date | De-energization Time (2400) | All Clear Declaration Date | All Clear Declaration Time (2400) | Restoration Date | Restoration Time (2400) | G.O. 95 Tier HFTD | Distribution/ Transmission Classification
Alpine | Muller 1296 | 2025-11-05 | 1:03 | 2025-11-05 | 14:29 | 2025-11-05 | 14:34 | 2 | Distribution
Mono | Topaz 1202 | 2025-11-05 | 1:03 | 2025-11-05 | 17:20 | 2025-11-05 | 17:22 | 2 | Distribution
Circuits De-Energized (continued)
County | Circuit Name | Residential Customers De-energized | Commercial / Industrial customers De-energized | Medical Baseline customers De-energized | AFN other than MBL customers De-energized | Total customers De-energized [3] | Restoration Time (2400) | G.O. 95 Tier HFTD | Other Customers
Alpine | Muller 1296 | 584 | 96 | 2 | 248 | 685 | 14:34 | 2 | 5
Mono | Topaz 1202 | 623 | 125 | 11 | 257 | 758 | 17:22 | 2 | 10
[3] Liberty’s post event report includes a lower customer count compared to its in-event reporting. This is because Liberty’s in-event reporting (i.e., initial count of customers) includes disconnected accounts and duplicate accounts. As seen during this event, Liberty’s initial customer count numbers may be higher than actuals as it reports the maximum potential impacted customers and attempts to communicate with as many customers as possible. Liberty’s customer notification system automatically suppresses duplicates and would not include notifications to disconnected accounts.

## Table 4-1
Table 4-1: Damage and Hazards Found
Circuit Name | Structure Identifier | County | G.O. 95 Tier HFTD | Type of Damage/ Hazard
Muller 1296 | Pole #214652 | Alpine | 2 | Broken insulator
Topaz 1202 | Pole #295108 | Mono | 2 | Object in the primary
Topaz 1202 | Pole #266633 | Mono | 2 | Object in the primary

## Table 5-1
Table 5-1: Description of PSPS Notifications
Type of Notification | Recipients | Description
Initial Notice for PSPS Event | PSPs and CFI (includes local and Tribal governments, hospitals, water/wastewater, telecommunications and transportation providers, CBOs) | Initial notification of potential PSPS event when circuits are first identified for potential deenergization.
All customers
Updated Notice for PSPS Event | PSPs and CFI (includes local and Tribal governments, hospitals, water/wastewater, telecommunications and transportation providers, CBOs) | Updated notification of potential PSPS event when circuits are first identified for potential deenergization.
All customers
Imminent De-energize (expected) | PSPs and CFI (includes local and Tribal governments, hospitals, water/wastewater, telecommunications and transportation providers, CBOs) | Power shutoff expected soon (1-4 hours before potential deenergization).
All customers
De-energized (shutoff) | PSPs and CFI (includes local and Tribal governments, hospitals, water/wastewater, telecommunications and transportation providers, CBOs) | Power has been shut off (when deenergization is initiated
All customers
Imminent Re-energize (prepare to restore) | PSPs and CFI (includes local and Tribal governments, hospitals, water/wastewater, telecommunications and transportation providers, CBOs) | Inspection/patrols of de-energized circuits for PSPS restoration has begun and power will be restored by estimated time.
All customers
Event concluded | PSPs and CFI (includes local and Tribal governments, hospitals, water/wastewater, telecommunications and transportation providers, CBOs) | Power has been restored and PSPS protocols are no longer enacted for this event.
All customers

## Table 5-2
Table 5-2: Notification Timeline
Event Order | Notification Type | Requirement Timeline | Notifications Sent To | Date Sent | Approximate Time Sent: Alpine County | Approximate Time Sent: Mono County
Pre-De-energization (prior) | Initial Notice for PSPS Event | 72-48 hours | N/A [4] | N/A | N/A | N/A
| Initial Notice for PSPS Event | 48-24 hours | PSP | 2025-11-03 | 15:15 | 15:15
|  | 48-24 hours | CFI | 2025-11-03 | 16:19 | 16:19
|  | 48-24 hours | MBL customers | 2025-11-03 | 16:19 | 16:19
|  | 48-24 hours | All other affected customers | 2025-11-03 | 16:19 | 16:19
|  | 48-24 hours | CalOES | 2025-11-03 | 15:30 | 15:30
|  | 48-24 hours | CPUC | 2025-11-03 | 15:34 | 15:34
| Updated Notice for PSPS Event | 12 hours prior | PSP | 2025-11-04 | 9:56 | 9:54
|  | 12 hours prior | CFI | 2025-11-04 | 9:35 | 9:35
|  | 12 hours prior | MBL customers | 2025-11-04 | 9:35 | 9:35
|  | 12 hours prior | All other affected customers | 2025-11-04 | 9:35 | 9:35
|  | 12 hours prior | CalOES | 2025-11-04 | 6:57 | 6:57
|  | 12 hours prior | CPUC | 2025-11-04 | 7:00 | 7:00
| Updated Notice for PSPS Event | 12 hours prior | PSP | 2025-11-04 | 15:42 | 15:45
|  | 12 hours prior | CFI | 2025-11-04 | 15:26 | 15:26
|  | 12 hours prior | MBL customers | 2025-11-04 | 15:26 | 15:26
|  | 12 hours prior | All other affected customers | 2025-11-04 | 15:26 | 15:26
|  | 12 hours prior | CalOES | 2025-11-04 | 15:00 | 15:00
|  | 12 hours prior | CPUC | 2025-11-04 | 15:00 | 15:00
| Imminent De-energize (expected) | 4-1 hours | PSP | 2025-11-04 | 21:22 | 21:22
|  | 4-1 hours | CFI | 2025-11-04 | 21:26 | 21:26
|  | 4-1 hours | MBL customers | 2025-11-04 | 21:26 | 21:26
|  | 4-1 hours | All other affected customers | 2025-11-04 | 21:26 | 21:26
|  | 4-1 hours | CalOES | 2025-11-04 | N/A | N/A
|  | 4-1 hours | CPUC | 2025-11-04 | N/A | N/A
In-Event (during) | De-energized | De-energization | PSP | 2025-11-05 | 9:24 | 9:25
|  | De-energization | CFI | 2025-11-05 | 1:11 | 1:11
|  | De-energization | MBL customers | 2025-11-05 | 1:11 | 1:11
|  | De-energization | All other affected customers | 2025-11-05 | 1:11 | 1:11
|  | De-energization | CalOES | 2025-11-05 | 1:06 and 6:53 | 1:06 and 6:53
|  | De-energization | CPUC | 2025-11-05 | 1:09 and 6:58 | 1:09 and 6:58
Restoration (after) | Imminent Re-energize (prepare to restore) | Imminent re-energization | PSP | 2025-11-05 | 12:18 | 14:14
|  | Imminent re-energization | CFI | 2025-11-05 | 12:26 | 15:00
|  | Imminent re-energization | MBL customers | 2025-11-05 | 12:26 | 15:00
|  | Imminent re-energization | All other affected customers | 2025-11-05 | 12:26 | 15:00
|  | Imminent re-energization | CalOES | 2025-11-05 | 14:57 | 14:57
|  | Imminent re-energization | CPUC | 2025-11-05 | 15:12 | 15:12
| Event concluded | All clear | PSP | 2025-11-05 | 14:47 | 17:41
|  | All clear | CFI | 2025-11-05 | 14:34 | 17:36
|  | All clear | MBL customers | 2025-11-05 | 14:34 | 17:36
|  | All clear | All other affected customers | 2025-11-05 | 14:34 | 17:36
|  | All clear | CalOES | 2025-11-05 | 18:00 | 18:00
|  | All clear | CPUC | 2025-11-05 | 18:02 | 18:02
[4] Liberty notified customers as soon as practicable. This notice was not provided because the rapid change in conditions (rather than any failure to notify) caused Liberty to provide this notice outside the minimum required timeline.

## Table 5-3
Table 5-3: Positive Notifications to MBL Customers
Category | Total Number of Customers | Timing of Attempts | Notification Attempts | Successful Positive Notification | Who Made the Notification
Medical Baseline | 13 | 11/3/2025 at 4:19 p.m. 11/4/2025 at approximately 10:00 a.m. 11/4/2025 at approximately 12:55-2:55 p.m. | 23 (Liberty continued to contact customers until positive notification) | 13 | Liberty

## Table 6-1
Table 6-1: Local and State Public Safety Partner Engagement
Entity Name | PSP Type | Organization | Title | HFTD Tier | Date Contacted | Time Contacted
Sean Landavazo | Fire | Cal Fire BUD | Deputy Chief` | 2 | 2025-11-03 | 15:46
Nate McCarthy | Fire | Cal Fire AEU | Battalion Chief | 2 | 2025-11-03 | 15:46
Tim Richter | Fire | Cal Fire NEU | Division Chief | 2 | 2025-11-03 | 15:46
Jim Hudson | Fire | Cal Fire NEU | Deputy Chief` | 2 | 2025-11-03 | 15:46
Shaun Fairbanks | Fire | Cal Fire SAC | Deputy Chief` | n/a | 2025-11-03 | 17:32
Chris Mokarcek | Emergency Mgmt | Mono Co | Emergency Manager | 2 | 2025-11-04 | 10:44
Chris Harootunian | Admin | Alpine Co | Public Health Program Manager | 2 | 2025-11-04 | 12:36
Evan Mecak | Admin | Alpine Co | Supervisor, District 2 | 2 | 2025-11-04 | 12:36
Tom Minder | Law | Alpine Co | Undersheriff | 2 | 2025-11-04 | 12:36
Nichole Williamson | Admin | Alpine Co | HHS Dir | 2 | 2025-11-04 | 12:36
Richard Johnson |  | Alpine Co | Pub Health Officer | 2 | 2025-11-04 | 12:36
Terry Hughes | Fire | Alpine Co | Fire Chief | 2 | 2025-11-04 | 12:36
Tim Streeper | Emergency Mgmt | Alpine Co | Emerg Prep | 2 | 2025-11-04 | 12:36
Craig Goodman | Admin | Alpine Co | Dir Finance | 2 | 2025-11-04 | 12:36
Angela Slais | Admin | Alpine Co | Public Health Program Manager | 2 | 2025-11-04 | 12:36
John Baker | Fire | Alpine Co | Alpine Co Fire Chief | 2 | 2025-11-04 | 12:36
Paul Washam | Law | Alpine Co | Alpine Co Sheriff | 2 | 2025-11-04 | 12:36
Irvin Jim | Admin | Alpine Co | Supervisor, District 3 (Hung-a-lel-Ti) | 2 | 2025-11-04 | 12:36
David Griffith | Admin | Alpine Co | Supervisor, District 5, Vice Chair | 2 | 2025-11-04 | 12:36
Michelle Beckwith |  | Alpine Co |  | 2 | 2025-11-04 | 12:36
Alison Hesterly | Fire | Cal Fire BDU | BDU PIO | 2 | 2025-11-04 | 12:36
Steve Elenburg | Fire | Cal Fire BDU | BDU Battalion Chief (Bishop) | 2 | 2025-11-04 | 12:36
Heidi Torix | Admin | ESUSD | Superintendent | 2 | 2025-11-04 | 12:36
Shane Gleason | Admin | ESUSD | Maintenance Dir | 2 | 2025-11-04 | 12:36
Shane Gleason | Admin | ESUSD | Maintenance Dir | 2 | 2025-11-04 | 12:36
Rich Nalder | Fire | Mono Co | Fire Chief | 2 | 2025-11-04 | 12:36
John Peters | Admin | Mono Co | Supervisor | 2 | 2025-11-04 | 12:36
Mike Martinez | Admin | Mono Co | IT Dir | 2 | 2025-11-04 | 12:36
Seth Clark | Law | Mono Co | Sheriff Lieutenant | 2 | 2025-11-04 | 12:36
Ingrid Braun | Law | Mono Co | Sheriff | 2 | 2025-11-04 | 12:36
Bryan Bullock | EMS | Mono Co | EMS Chief | 2 | 2025-11-04 | 12:36
Sarah Roberts | Law | Mono Co | Sheriff's Dept PIO | 2 | 2025-11-04 | 12:36
Sandra Moberly | Admin | Mono Co | Chief Administrative Officer | 2 | 2025-11-04 | 12:36
Michael Lightfoot | Fire | Mono Co MWTC | Asst. Fire Chief | 2 | 2025-11-04 | 12:36
Andrew Oddo |  | Mono Co MWTC |  | 2 | 2025-11-04 | 12:36
Kathy Peterson | Admin | Mono Co Social Services | Director | 2 | 2025-11-04 | 12:36
Cathy Young | Admin | Mono Co Social Services | Shelter Coordinator Lead | 2 | 2025-11-04 | 12:36
Leslie Gaunt | Admin | Mono Co Social Services | Shelter Coordinator | 2 | 2025-11-04 | 12:36
Yvonne Freeman | Admin | Mono Co Social Services | Shelter Coordinator | 2 | 2025-11-04 | 12:36
Cassidy Miles | Admin | Mono County HHS / Social Services | Senior Services Supervisor | 2 | 2025-11-04 | 12:36
Bri Chappell-McGovern | Emergency Mgmt | Mono County Public Health | Emergency Preparedness Manager | 2 | 2025-11-04 | 12:36
Jacob Maxwell | Military | USMC |  | 2 | 2025-11-04 | 12:36
Ken Quiner | Tribal | Washoe Tribe | Tribal Emergency Manager | 2 | 2025-11-04 | 12:36
Robert Beltramo | Tribal | Washoe Tribe | Tribal Planning Director | 2 | 2025-11-04 | 12:36
Lisa Christensen | Tribal | Washoe Tribe | Washoe Tribe Emergency Manager | 2 | 2025-11-04 | 12:36
George Abbott | Tribal | Washoe Tribe |  | 2 | 2025-11-04 | 12:36
Max Rettig | Tribal | Washoe Tribe |  | 2 | 2025-11-04 | 12:36
Geoff Ellis | Tribal | Washoe Tribe | Hung A Lel Ti Community Chairman | 2 | 2025-11-04 | 12:36

## Table 7-1
Table 7-1: Count and Nature of Complaints Received
Nature of Complaints | Complaint Format | Number of Complaints
Communications | In person | 2
Communications | Phone Call | 1
Restoration questions | In Person | 2
Resources/needs unmet | In Person | 2

## Table 9-1
Table 9-1: Community Resource Centers
# | County | Site Name | Address | Operating Hours | Attendance | Site Type | Services and Amenities Provided
1 | Alpine | Woodfords Community Center | 25 Washo Blvd, Markleeville, CA 96120 | 11/05/2025, 8a.m.-5p.m. | 72 | CRC - Building | Small portable device charging (for cell phone, laptop, and small medical devices), Wi-Fi, chairs, seasonal cooling, and heating, PSPS information, snacks, water, ice, ADA compliant restrooms.
1 | Mono | Walker Community Center | 442 Mule Deer Drive, Walker, CA 93517 | 11/05/2025, 8a.m.-5p.m. | 25 | CRC - Building | Small portable device charging (for cell phone, laptop, and small medical devices), Wi-Fi, chairs, seasonal cooling, and heating, PSPS information, snacks, water, ice, ADA compliant restrooms.

## Table 10-1
Table 10-1: Grid Hardening Activities Completed to Mitigate PSPS Impact
Circuit | Poles Installed | ELF Fuses Installed | Overhead Primary Conductor Replaced (ft.) | Overhead Secondary Conductor Replaced (ft.) | Composite Crossarms Installed | Transformers Installed
Muller 1296 | 156 | 24 | 16026 | 3714 | 98 | 21
Topaz 1202 | 127 | 35 | 13307 | 972 | 103 | 20

## Table 11-1
Table 11-1: Lessons Learned
Issue | Discussion | Resolution
State Executive Briefing presentation template | Use different template for State Executive Briefing after de-energization has occurred. | Liberty will use the correct template for future State Executive Briefings.
CalOES submission form | CalOES form entry for customers potentially impacted should go to 0 once those customers are actually impacted. | Liberty has discussed this issue with CalOES and is clear on this guidance moving forward.
Positive feedback | Track positive feedback received from stakeholders in internal event tracker during event. | Liberty will include this information in the event tracker for future events.
Notification forms | Include estimated time of restoration on all notifications during event; include CRC services available and where to access electricity during the hours the CRC is closed on customer notifications. | Liberty will adapt its notification templates to include estimated time of restoration and CRC services available; Liberty is assessing the requirement to include information on where to access electricity during the hours CRCs are closed.
Cost tracking codes | Internal cost tracking codes were not sufficiently explained until after the PSPS event. | Publish cost tracking codes with explanations in Incident Action Plan prior to or in the beginning of the event.
Ancillary internal map | Ancillary map was needed to inform internal staff of potential threat in the community (previously documented difficult customer). | Establish needs for ancillary maps for operations and field employees.
Customer discrepancies | In-event customer numbers were different than post-event reporting due to duplicate and de-activated customer accounts included in in-event reporting. | Liberty will update its PSPS playbook to document its process for removing duplicate and de-activated customer accounts for in-event reporting.
CRC staffing | Recent staffing changes have impacted list of CRC leads. | Reassess list of CRC leads to address recent staffing changes.
CRC signage | There were no signs at the CRC locations. | Put up signs outside CRC locations during future PSPS events.
IMT roles | Liberty has a vacancy for the Emergency Manager Position | Liberty is actively in the hiring process to fill the Emergency Manager Position.
CRC Supplies | A couple customers requested larger sized bottles of water for toilet flushing. | Determine if there is a reasonable solution to better prepare customers using well water